Product Specification Guide
Model Motor Starter Single Phase (MS1P)

************************************************************************************************************************
Note to User: This document is subject to copyright protection and is proprietary to Greenheck Fan Corporation.  However, Greenheck Fan Corporation authorizes the user a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category.  All information in this document as provided by Greenheck Fan Corporation is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, ANY IMPLIED WARRANTY OF MERCHANTABILITY, FITNESS FOR PARTICULAR PURPOSE, OR NON-INFRINGEMENT.  To the greatest extent permitted by applicable law, Greenheck Fan Corporation assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not.  Users should consult www.greenheck.com to verify that this document represents the most current version.
************************************************************************************************************************

The single phase motor starter shall consist of a manually operated quick-make toggle mechanism lockable in the “of” position which can also function as the motor disconnect if necessary. The starter shall provide field adjustable thermal overload protection, a Normally Open auxiliary control contact as well as power, run and fault status pilot lights. The starter must include the capability to operate in both manual and automatic control modes. When remotely controlled by an automation system, thee starter shall include a remote run terminal which accepts a voltage input signal which accepts both AC and DC SIGNALS INCLUDING 24VAC, 120VAC, 24VDC and 48VDC to allow direct connection of the transistorized automation signal to the starter. Starter must contain an integral current sensor with Normally Open contact which closes to indicate motor run status as well as a Normally Open contact which closes when an overload trip condition occurs. 

The starter shall be UL listed.

Starters shall be Model MS1P as manufactured by Greenheck.