Product Specification Guide
Model SB-2, Belt Drive Sidewall Mounted Propeller Fan 
Facility Services Subgroup: Division 23 Section 23 34 23

Note to User: This document is subject to copyright protection and is proprietary to Greenheck Fan Corporation. However, Greenheck Fan Corporation authorizes the user a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category. All information in this document as provided by Greenheck Fan Corporation is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, ANY IMPLIED WARRANTY OF MERCHANTABILITY, FITNESS FOR PARTICULAR PURPOSE, OR NON-INFRINGEMENT. To the greatest extent permitted by applicable law, Greenheck Fan Corporation assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not. Users should consult www.greenheck.com to verify that this document represents the most current version.

*************************************************************************************************************
Specifier Notes: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Format - 2004 Edition.

This section must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code. Coordinate with other specification sections and the drawings.

Delete all unnecessary “Specifier Notes” when editing this section.
*************************************************************************************************************

1.	GENERAL

1.1	SUMMARY

A.	Section Includes: HVAC Power Ventilators
B.	Related Sections:
*************************************************************************************************************
Specifier Notes: Delete any sections below not relevant to this project; add others as required.
*************************************************************************************************************
1.	01 00 00 General Requirements
2.	07 00 00 Thermal and Moisture Protection
3.	09 00 00 Finishes
4.	23 00 00 Heating, Ventilating, and Air-Conditioning (HVAC)
5.	26 00 00 Electrical

1.2	REFERENCES

*************************************************************************************************************
Specifier Notes: Delete references from the list below that are not actually required by the text of the edited section.
*************************************************************************************************************
A.	Air Movement and Control Association Inc. (AMCA):
1.	99 – Standards Handbook
2.	200 – Publication, Air Systems
3.	201-90 – Publication, Fans and Systems
4.	202-88 – Publication, Troubleshooting
5.	203-90 – Publication, Field Performance Measurement of Fan Systems
6.	211-05 – Publication, Certified Ratings Program – Product Rating Manual for Fan Air Performance
7.	300-96 – Standard Reverberant Room Method for Sound Testing of Fans
8.	311-05 – Publication Certified Ratings Program – Product Rating Manual for Fan Sound Performance
9.	99-0401-86 – Classification for Spark Resistant Construction
10.	99-2408-69 – Operating Limits for Centrifugal Fans
B.	American National Standards Institute/Air Movement and Control Association Inc. (ANSI/AMCA ﻿Standard):
1.	204-20 – Balance Quality and Vibration Levels for Fans
2.	210-25 – Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating
C.	American National Standards Institute (ANSI):
1.	11-r1999 – Method of Evaluating Load Ratings of Bearings 
D.	American Society of Civil Engineers (ASCE):
1.	7-02 – Minimum Design Loads for Building and Other Structures
E.	American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE):
1.	Chapter 45 – 2003 Handbook, HVAC Applications
2.	Chapter 7 – 2001 Fundamentals handbook, Sound-Vibration
3.	Chapter 32 – 2001 Fundamentals handbook, Duct Design
4.	Chapter 18 – 1992 HVAC System and Equipment handbook, Fans
F.	American Society for Testing and Materials (ASTM):
1.	E330-02 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylight and Curtain Walls by Uniform Static Air Pressure Difference
G.	National Fire Protection Association (NFPA):
1.	70 – National Electrical Code
2.	90A-02 – Standard for the Installation of Air-Conditioning and Ventilating Systems
3.	92A-06 – Recommend Practice for Smoke-Control System
4.	92B-05 – Standard for Smoke Management System in Malls, Atria, and Large Areas
5.	96-04 – Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations
H.	Occupational Safety and Health Administration (OSHA):
1.	1910.212 – General requirements for Machine Guarding
2.	1910.219 – General requirements for guarding safe use of mechanical power transmission apparatus
3.	1926.300 – General requirements for safe operation and maintenance of hand and power tools
I.	Underwriters Laboratories (UL):
1.	507 – Electric Fans
2.	555 – Fire Dampers
3.	555S – Smoke Dampers
4.	705 – Standard Power Ventilators
5.	705 – Supplement SC - Standard Power Roof Ventilators for Restaurant Exhaust Appliances
6.	793 – Snow Load

1.3	SUBMITTALS

A.	General: Submit in accordance with Section 01 33 00 Submittal Procedures.
B.	Provide dimensional drawings and product data for each fan.
C.	Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.
D.	Provide outlet velocity and fan's inlet sound power readings for the eight octave bands, decibels, and sones.
E.	Strictly adhere to QUALITY ASSURANCE requirements as stated in section 1.4 of this specification.
F.	Provide manufacturer's certification that supply and exhaust fans are licensed to bear Air Movement and Control Association (AMCA), Certified Rating Seal for FEI, Sound and Air Performance.
G.	Provide fan FEI value on design documents and product submittals when operating power is greater than or equal to 1 hp.
H.	Installation, Operation, and Maintenance Manual (IOM): Provide manufacturer's installation, operations, and maintenance manual, including instructions on installation, operations, maintenance, pulley adjustment, receiving, handling, storage, safety information and cleaning. A troubleshooting guide, parts list, warranty and electrical wiring diagrams.

1.4	QUALITY ASSURANCE

A.	Performance ratings: Conform to AMCA standard 211 and 311. Fans must be tested in accordance with ANSI/AMCA Standard 210-16 and AMCA Standard 300-14 in an AMCA accredited laboratory. Fans shall be certified to bear the AMCA label for sound, air, and FEI performance seal.
B.	Fans shall have a Fan Energy Index (FEI) rating that meets or exceeds requirements of the latest edition of ASHRAE 90.1.
C.	Classification for Spark Resistant Construction, levels A, B and C, conform to AMCA 99.
D.	Each fan propeller is balanced in order to meet a Balance Grade of 6.3.
E.	Comply with the National Electrical Manufacturers Association (NEMA), standards for motors and electrical accessories.
F.	The Finite Element Analysis (FEA) is the results from the CFD and it can accurately predict the stress, strain, and deflection resulting from high wind loads.

1.5	DELIVERY, STORAGE, AND HANDLING

A.	Delivery: Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer, material, products included, and location of installation.
B.	Storage: Store materials in a dry area indoor, protected from damage, and in accordance with manufacturer’s instructions. For long term storage follow manufacturer's Installation, Operations, and Maintenance Manual.
C.	Handling: Handle and lift fans in accordance with the manufacturer’s instructions. Protect materials and finishes during handling and installation to prevent damage. Follow all safety warnings posted by the manufacturer.

1.6	WARRANTY

A.	Manufacturer's Warranty: Submit, for Owner's acceptance, manufacturer's standard warranty document executed by authorized company official. Manufacturer's warranty is in addition to, and not a limitation of, other rights Owner may have under Contract Documents.
1.	The warranty of this equipment is to be free from defects in material and workmanship for a period of one year from the purchase date. Any units or parts which prove defective during the warranty period will be replaced at the Manufacturers option when returned to Manufacturer, transportation prepaid.
2.	Motor Warranty is warranted by the motor manufacturer for a period of one year. Should motors furnished by us prove defective during this period, they should be returned to the nearest authorized motor service station.

1.7	MAINTENANCE

A.	Refer to Manufacturer's Installation, Operation and Maintenance Manual (IOM), to find maintenance procedures.

2.	PRODUCTS

2.1	MANUFACTURER

A.	Greenheck, PO Box 410, Schofield, Wisconsin 54476
Phone: (715) 359-6171  Fax: (715)355-2399  Website: www.greenheck.com

2.2	BELT DRIVE SIDEWALL MOUNTED PROPELLER FAN - GREENHECK 
MODEL SB-2

A.	General Description:
*************************************************************************************************************
Specifier Note: Fan arrangement includes supply and exhaust modes. Consult manufacturer for additional information.
*************************************************************************************************************
1.	Fan arrangement shall be either supply or exhaust, see Fan Schedule.
2.	Sidewall mounted applications.
3.	Performance capabilities up to 53,200 cubic feet per minute (cfm) and static pressure to 1 inch of water gauge.
4.	Fans are available in eight sizes with nominal propeller diameters ranging from 20 inches through 54 inches (20 - 60 unit sizes).
5.	Maximum continuous operating temperature 130° Fahrenheit (54.4° Celsius) with appropriate motor selection.
6.	Each fan shall bear a permanently affixed manufacture's engraved metal nameplate containing the model number and individual unit serial number.
B.	Propeller:
*************************************************************************************************************
Specifier Note: Edit the following wheel material to fit the requirements of the project. Consult manufacturer for additional information.
1.	L - Type (low pressure) – Propeller is a fabricated steel propeller (aluminum optional) with a swept, steeply pitched blade design. Typically run at lower RPM's and generate low sound levels.
2.	H - Type (high pressure) – Propeller is a fabricated steel propeller (aluminum optional) with a straight, moderately pitched blade. Typically run at higher RPM's and generate higher sound levels than the "L" propeller.
*************************************************************************************************************
1.	Constructed of: [Aluminum] [Steel] blades and hubs
2.	Securely attached to motor shaft with a standard square key and set screw or tapered bushing.
3.	Statically and dynamically balanced in accordance with AMCA Standard 204-05.
4.	The propeller and fan inlet will be aligned and shall have precise running tolerances for maximum performance and operating efficiency.
5.	Propellers are not coated when fan coatings accessory is selected regardless of material type.
C.	Motor: 
*************************************************************************************************************
Specifier Note: Edit the following motor enclosures to meet project requirements. Consult manufacturer for additional information.
1.	Open Drip-Proof (ODP) – Opening in the frame body and or end brackets.
2.	Totally Enclosed Fan Cooled (TEFC) – No opening in the frame or brackets. Equipped with an external fan to blow air over the motor.
3.	Explosion Resistant Enclosure (EXP) – Totally enclosed motor, with a housing constructed to contain any explosion within the motor caused by the hazardous atmosphere entering the enclosure and being ignited.
*************************************************************************************************************
1.	Motor Enclosure: [Open Drip-Proof] [Totally Enclosed Fan Cooled] [Explosion Resistant Enclosure]
2.	Motors are permanently lubricated, heavy duty ball bearing type to match with the fan load and pre-wired to the specific voltage and phase.
3.	Accessible for maintenance.
D.	Shaft and Bearings:
1.	Fan shaft shall be ground and polished solid steel with an anti-corrosive coating.
2.	Bearing shall be stamped steel or cast pillow block.
3.	Bearings shall be selected for a minimum L10 life in excess of 100,00 hours (equivalent to L50 average life of 500,000 hours), at maximum cataloged operating speed.
4.	Bearing shall be air handling quality and 100% factory tested by bearing manufacturer.
5.	Fan shaft first critical speed is at least 25 percent over maximum operating speed.
E.	Drive Frame:
1.	Drive frame assemblies shall be galvanized steel, and bolted construction.
2.	Drive frame shall have formed channels and fan panels shall have pre-punched mounting holes, formed flanges and a deep formed one piece inlet venturi.
F.	Disconnect Switch:
*************************************************************************************************************
Specifier Notes: Edit the following Disconnect Switches to meet project requirements. Factory Mounted and Shipped loose for field mounting, National Electrical Manufacturers Association (NEMA). Consult manufacturer for additional information.
1.	NEMA 1 – Indoor application no water. 
2.	NEMA 3R – Outdoor application falling rain water.
3.	NEMA 4 – Outdoor application hose directed water.
4.	NEMA 4X – Same as NEMA 4, but corrosion resistant.
5.	NEMA 7 and 9 – Explosion resistant indoor and outdoor use.
6.	NEMA 12 – Industrial use, dust-tight, and drip-tight, oil resistant for indoor use.
*************************************************************************************************************
1.	NEMA Rated: [1] [3R] [4] [4X] [7&9] [12]
2.	Positive electrical shut-off.
3.	Wired from fan motor to junction box. 
G.	Drive Assembly: 
1.	Belts, pulleys, and keys oversized for a minimum of 150 percent of driven horsepower.
2.	Belt: Static free and oil resistant.
3.	Fully machined cast iron pulleys, keyed and securely attached to the wheel and motor shafts.
4.	The drive systems are preset at the factory for the specified fan RPM. 
5.	Readily accessible for maintenance.
H.	Options/Accessories:
*************************************************************************************************************
Specifier Notes: Specify accessories 1-9 required for the fans. Delete accessories not required. Consult manufacturer for additional information.
*************************************************************************************************************
1.	Closure Angles:
a.	Set of mounting flanges shall be available for field installation to close off the interior wall opening for a finished appearance.
2.	Damper:
*************************************************************************************************************
Specifier Notes: Specify gravity or motorized backdraft dampers. Specify damper size based on specified fan size. Consult manufacturer for additional information.
*************************************************************************************************************
a.	Type: [Gravity] [Motorized]
b.	Prevents outside air from entering back into the building when fan is off.
c.	Balanced for minimal resistance to flow.
d.	Galvanized frames with pre-punched mounting holes.
3.	Damper Guard:
*************************************************************************************************************
Specifier Notes: Edit the following damper guard material to meet project requirements. Guards meet OSHA requirements. Consult manufacturer for additional information.
*************************************************************************************************************
a.	Guard Frame Material: [Galvanized] [Aluminum]
b.	Shall completely enclose the damper or wall opening on the discharge side of the fan.
4.	Finishes:
*************************************************************************************************************Specifier Notes: Edit the following finishes to meet project requirements. Consult manufacturer for additional information. 
a.	Permatector – Thermo-setting polyester urethane.
b.	Hi-Pro Polyester – Meets or exceeds the chemical resistance properties of Air Dry Phenolic (Heresite).
c.	Industrial Epoxy – Indoor, thermosetting epoxy powder with chemical resistance to a wide variety of chemicals, grey color.
*************************************************************************************************************
a.	Type: [None] [Permatector] [Hi-Pro Polyester] [Industrial Epoxy]
5.	Horizontal Mounting:
*************************************************************************************************************
Specifier Notes: Edit the following mounting locations to meet project requirements. Consult manufacturer for additional information.
*************************************************************************************************************
a.	Allows fan to be mounted in a horizontal configuration.
b.	Location: [Motor Top, Air Down] [Motor Bottom, Air Up] [Motor Top, Air Up] [Motor Bottom, Air Down]
6.	Wall Housing:
*************************************************************************************************************
Specifier Notes: Edit the following mounting arrangements to meet project requirements. Consult manufacturer for additional information.
a.	Flush Interior – Housing ships with angles mounted so unit mounts flush to the interior wall.
b.	Flush Exterior – Housing ships with angles mounted so unit mounts flush to exterior wall.
c.	Motor Access Interior – Allows servicer to gain easy access to the motor from interior of building.
d.	Motor Access Exterior – Allows servicer to gain easy access to the motor from exterior of building.
*************************************************************************************************************
a.	Mounting arrangement: [Flush Interior] [Flush Exterior] [Motor Access Interior] [Motor Access Exterior]
b.	Constructed of galvanized steel or painted steel with heavy gauge mounting flanges and pre-punched mounting holes.
c.	Housing shall include OSHA approved motor guard.
d.	Reduces installation time and provides maximum installation flexibility.
7.	Wall Collar:
a.	Constructed of galvanized steel or painted steel with heavy gauge mounting flanges and pre-punched mounting holes.
8.	Motor Side Guard:
a.	Guard Type: OSHA Approved
b.	Protective guard of expanded metal screen in structural steel frames completely enclose the motor and drive side of the fan.
9.	Weatherhood Kit:
*************************************************************************************************************
Specifier Notes: Edit the following weatherhood accessories items to meet project requirements. Consult manufacturer for additional information.
a.	Turndown Angles – 45 degrees is for exhaust only, 90 degrees is for both exhaust and supply.
b.	Birdscreen – 1/2 inch by 1/2 inch weld wire.
c.	Insect Screen – 16 to 18 inch aluminum mesh.
*************************************************************************************************************
a.	Shall shield wall opening and dampers from rain and snow.
b.	Frame Material Type: [Galvanized] [Aluminum]
c.	Turndown Angle: [45] [90] degrees
d.	Screen: [Galvanized Birdscreen] [Insect screen]
e.	Finishes: [None] [Permatector] [Hi-Pro Polyester] [Industrial Epoxy]

3.	EXECUTION

3.1	MANUFACTURER'S INSTRUCTIONS

A.	Compliance: Comply with manufacturer's product data, including technical bulletins, product catalog installation instructions.

3.2	EXAMINATION

A.	Examine areas to receive fans. Notify the Engineer of conditions that would adversely affect installation or subsequent utilization and maintenance of fans. Do not proceed with installation until unsatisfactory conditions are corrected.

3.3	PREPARATION

A.	Ensure roof openings are square, accurately aligned, correctly located, and in tolerance.
B.	Ensure duct is plumb, sized correctly, and to proper elevation above roof deck. Install duct as specified in Air Distribution (Division 23).

3.4	INSTALLATION

A.	Install fans system as indicated on the Installation, Operation and Maintenance Manual (IOM) and contract drawings.
B.	Install fans in accordance with manufacturer's instructions.

3.5	SYSTEM STARTUP

A.	Refer to Installation, Operation, and Maintenance Manual (IOM).

3.6	ADJUSTING

A.	Adjust fans to function properly.
B.	Adjust Belt Tension.
C.	Lubricate bearings.

3.7	CLEANING

A.	Clean as recommended by manufacturer. Do not use material or methods which may damage finish surface or surrounding construction.

3.8	PROTECTION

A.	Protect installed product and finished surfaces from damage during construction.
B.	Protect installed fans to ensure that, except for normal weathering, fans will be without damage or deterioration at time of substantial completion.

END OF SECTION 23 34 23