Product Specification Guide
Tube Axial Inline Belt Drive Fans, Model TBI-FS
Facility Services Subgroup: Division 23 (Previously Division 15)

************************************************************************************************************************
Specifier Notes: This product specification guide is written according to the Construction Specifications Institute (CSI) Format.

This section must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code. Coordinate with other specification sections and the drawings.

Delete all unnecessary “Specifier Notes” when editing this section. 

Note to User: This document is subject to copyright protection and is proprietary to Greenheck Fan Corporation. However, Greenheck Fan Corporation authorizes the user a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category. All information in this document as provided by Greenheck Fan Corporation is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, ANY IMPLIED WARRANTY OF MERCHANTABILITY, FITNESS FOR PARTICULAR PURPOSE, OR NON-INFRINGEMENT. To the greatest extent permitted by applicable law, Greenheck Fan Corporation assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not. Users should consult www.greenheck.com to verify that this document represents the most current version.
************************************************************************************************************************

PART 1	 GENERAL
1.1 	WORK INCLUDED 
A.	Tube Axial Inline Belt Drive Fabricated Steel Propeller Fan, Model TBI-FS

1.2 	RELATED SECTIONS 
A.	All sections, drawing plans, specifications and contract documents.

1.3 	REFERENCES
A.	ANSI/AMCA Standard 99-10, “Standards Handbook” 
B.	ANSI/AMCA Standard 204-05, “Balance Quality and Vibration Levels for Fans”
C.	ANSI/AMCA Standard 210-07, “Laboratory Methods of Testing Fans for Aerodynamic Performance Rating”
D.	AMCA Publication 211-05, “Certified Ratings Program – Product Rating Manual for Fan Air Performance”
E.	ANSI/AMCA Standard 300-08, “Reverberant Room Method for Sound Testing of Fans”
F.	AMCA Publication 311-05, “Certified Ratings Program – Product Rating Manual for Fan Sound Performance”
G.	AMBA - Method of Evaluating Load Ratings of Bearings ANSI-11 (r1999).
H.	ANSI/AMCA Standard 500-D-12, “Laboratory Methods of Testing Dampers for Rating”
I.	OSHA guideline 1910.212 – General requirements for Machine Guarding. (www.osha.gov)
J.	OSHA guideline 1910.219 – General requirements for guarding safe use of mechanical power transmission apparatus. (www.osha.gov)
K.	OSHA guideline 1926.300 – General requirements for safe operation and maintenance of hand and power tools. (www.osha.gov)
L.	UL Standard 705, “Power Ventilators”

****************************************************************************************************************************
Specifier Notes: 

Fans shall be UL/cUL listed as “Power Ventilators for Smoke Control Systems” (by maximum temperature for a minimum number of hours of operation) for one of the following.  

1.	300F (149C) maximum temperature for a minimum of 5 hours of operation
2.	750F (399C) maximum temperature for a minimum of 4 hours of operation
3.	1000F (538C) maximum temperature for a minimum of 15 minutes of operation

The UL Power Ventilators for Smoke Control sticker shall be fixed to the fan housing. 

****************************************************************************************************************************

1.4 	QUALITY ASSURANCE
A.	Performance ratings: Conform to ANSI/AMCA Standards 210 and 300. Fan must be tested in accordance with AMCA Publications 211 and 311 in an AMCA accredited laboratory and certified for sound and air performance. Fan shall be licensed to bear the AMCA ratings seal for air performance (AMCA 210) and sound performance (AMCA 300). 
B.	Classification for Spark Resistant Construction shall conform to ANSI/AMCA Standard 99.
C.	Fan shall be UL/cUL listed for emergency heat and smoke removal.

1.5	SUBMITTALS
A.	Provide dimensional drawings and product data on each tube axial fan.
B. 	Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.
C.	Provide outlet velocity of axial fan and both inlet and outlet sound power readings for the eight octave bands. 
D.	Strictly adhere to QUALITY ASSURANCE requirements as stated in section 1.4 of this specification

1.6	DELIVERY, STORAGE, AND HANDLING
A.	Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer, material, products included, and location of installation.
B.	Store materials in a dry area indoor, protected from damage, and in accordance with manufacturer’s instructions. For long term storage, follow manufacturer’s Installation, Operation and Maintenance manual.
C.	Handle and lift fans in accordance with the manufacturer’s instructions. Protect materials and finishes during handling and installation to prevent damage. Follow all safety warnings posted by the manufacturer.

1.7	WARRANTY
A.	Submit, for Owner's acceptance, manufacturer's standard warranty document executed by authorized company official. Manufacturer's warranty is in addition to, and not a limitation of, other rights Owner may have under Contract Documents.
1.	The warranty of this equipment is to be free from defects in material and workmanship for a period of 12 months from the purchase date. Any units or parts which prove defective during the warranty period will be replaced at the manufacturers’ option when returned to the manufacturer, transportation prepaid.
2.	Motor Warranty is warranted by the motor manufacturer for a period of one year. Should motors furnished prove defective during this period, they should be returned to the nearest authorized motor service station.

PART 2 EQUIPMENT
2.1	GENERAL
A. 	Base fan performance at standard conditions (density 0.075 Lb. /ft3).
B.	Fans selected shall be capable of accommodating static pressure and flow variations of +/-15% of scheduled values.
C.	Each fan shall be belt in AMCA arrangement 9 with propeller secured to the motor shaft. 
D.	Fans are to be equipped with lifting lugs.
E.	After fabrication all carbon steel components shall be cleaned and chemically treated by a phosphatizing process to insure proper removal of grease, oil, scale, etc. Fan shall then be coated with a minimum of 2-4 mils of Permatector (Polyester Urethane), electrostatically applied and baked. Finish color shall be RAL 7023, concrete grey. Coating must exceed 1,000-hour salt spray under ASTM B117 test method.

2.2	FAN HOUSING AND OUTLET
A.	Fan housing shall be constructed of continuously welded steel and include an integral punched inlet and outlet flange to prevent air leakage.
B.	Fans shall incorporate universal a mounting system to allow for field transitions from horizontal base mount, horizontal ceiling hung, vertical base mount or vertical ceiling hung configurations.
D.	Housing and bearing support shall be constructed of welded structural steel members to prevent vibration and rigidly support the shaft and bearings.
E.	Belts, bearings and drives shall be protected from the airstream by heavy gauge steel belt tubes bolted bearing covers.
F.	Either an OSHA compliant weatherhood, or an OSHA compliant belt guard shall be included to completely cover the motor pulley and belt(s).

2.3	FAN WHEEL
A.	The fan propeller shall be fabricated steel available in two levels of construction and include “Low and High” pressure blade pitch angles. Airfoil blades shall be continuously welded to heavy duty hubs to ensure long life in the harshest commercial or industrial applications.
B.	A standard square key or tapered bushing shall lock to propeller to the fan shaft. Hubs shall be two piece aluminum castings that securely lock the blades in place.
C.	Wheels shall be statically and dynamically balanced to balance grade G6.3 per ANSI S2.19.
D.	Aluminum propeller parts shall not require protective coatings.
E.	The wheel and fan inlet shall be carefully matched and shall have precise running tolerances for maximum performance and operating efficiency. 

2.4	FAN MOTORS AND DRIVE
A.	Motors shall meet or exceed EPACT (Energy Policy ACT) efficiencies. Motors to be NEMA T-frame, 1800 or 3600 RPM, Open Drip Proof (ODP) [Totally Enclosed Fan Cooled (TEFC), Explosion Proof (EXP) with a 1.15 service factor. 
B.	Drive belts and sheaves shall be sized for 150% of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required. 
C.	Fan shaft to be turned and polished steel that is sized so the first critical speed is at least 25% over the maximum operating speed for each pressure class.
D.	Fan shaft bearings shall be Air Handling Quality, bearings shall be heavy-duty grease lubricated, self-aligning or roller pillow block type. 
E.	Air Handling Quality bearings to be designed with low swivel torque to allow the outer race of the bearing to pivot or swivel within the cast pillow block. Bearings shall be 100% tested for noise and vibration by the manufacturer. Bearings shall be 100% tested to insure the inner race diameter is within tolerance to prevent vibration.
F.	Bearings shall be selected for a basic rating fatigue life (L-10) of 80,000 hours at maximum operating speed for each pressure class {Average Life or (L-50) of 400,000 hours} for horizontal mount and a basic rating fatigue life L(10) of 40,000 hours at maximum operating speed {Average Life or (L-50) of 200,000 hours} for vertical mount. 
G.	Bearings shall be fixed to the fan shaft using concentric mounting locking collars, which reduce vibration, increase service life, and improve serviceability. Bearings that use set screws shall not be allowed. 
H.	Bearings shall have Zerk fittings to allow for lubrication.

PART 3 EXECUTION
3.1	EXAMINATION
A.	Examine areas to receive fans. Notify the Engineer of conditions that would adversely affect installation or subsequent utilization and maintenance of fans. Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	INSTALLATION
A. 	Install fans systems as indicated on the contract drawings.
B. 	Install fans in accordance with manufacturer’s Installation, Operation and Maintenance manual.

PART 4 ACCEPTABLE MANUFACTURERS
A.	Greenheck Fan Corporation, PO Box 410, Schofield WI 54476-0410, www.greenheck.com  
    Model TBI-FS, Tube Axial Inline Fans.