## BTD contractor sched 10 in-wg
Bubble Tight Damper Schedule
| General Details | [5 empty] | Mtg Hole Details |  |  |  |  | Actuator Details
| Damper ID | Damper Qty | Damper Diameter (inches) | Damper Design Pressure (in-wg) | Damper Material (Painted, 304SS, 316SS) | Basis of Design | Mtg Holes Required? (Y or N) | Qty of Holes | Hole Dia | Bolt Circle Dia | straddling Vertical CL or On Vertical CL | Actuator Type | Power Supply | Actuator Operation (PO/PC or Spring return) | If Spring return, fail open or fail closed | Auxiliary Switches Required (Y or N) | Nema Enclosure (1, 4, 4x, 7 or 9)
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
|  |  |  | 10 |  | Greenheck HBTR-151
Option 1 | Suggested Construction Notes: Dampers shall be rated to 10 in-wg pressure Dampers shall be tested to AMCA 500D for bubble tight effectiveness before shipment Manufacture Dampers in an ISO9001 certified facility Design Temperature is a maximum temperature of 250°F Dampers shall have fully welded construction and have full length damper shafts Dampers shall have been prototype tested to 10,000 open and closed cycle tests to confirm durability Dampers shall have double gland shaft seals. Press-fit lip seals are not acceptable. Basis of Design: Greenheck, Model HBTR-151 | [5 empty] | Mounting Hole Note: "Manufacturer Standard" is a valid entry |  |  |  |  | Actuator Types: Electric: 24VAC, 24VDC, 120VAC, 230VAC Pneumatic: 80PSI Manual: Quadrant, Handwheel, Chainwheel Bracket Only: supplied with (2) mtg angles for field supplied actuators. Actuator Notes: bracket-only option works well for commercial grade actuators, field supplied industrial actuators are not recommended. Power Open/Power Closed actuator option will Fail In Place on loss of power
Option 2 | [6 empty] | Mounting Hole Note:
"Manufacturer Standard" is a valid entry
| Suggested Construction Notes: | [10 empty] | Actuator Types:
| Dampers shall be rated to 10 in-wg pressure | [10 empty] | Electric: 24VAC, 24VDC, 120VAC, 230VAC
| Dampers shall be tested to AMCA 500D for bubble tight effectiveness before shipment | [10 empty] | Pneumatic: 80PSI
| Manufacture Dampers in an ISO9001 certified facility | [10 empty] | Manual: Quadrant, Handwheel, Chainwheel
| Design Temperature is a maximum temperature of 250°F | [10 empty] | Bracket Only: supplied with (2) mtg angles for field supplied actuators.
Dampers shall have fully welded construction and have full length damper shafts
| Dampers shall have been prototype tested to 10,000 open and closed cycle tests to confirm durability | [10 empty] | Actuator Notes:
| Dampers shall have double gland shaft seals. Press-fit lip seals are not acceptable. | [10 empty] | bracket-only option works well for commercial grade actuators, field supplied industrial actuators are not recommended.
| Basis of Design: Greenheck, Model HBTR-151 | [10 empty] | Power Open/Power Closed actuator option will Fail In Place on loss of power
what about AG-1 call out somewhere?