## BTD contractor sched 40 in-wg
Bubble Tight Damper Schedule
General Details | [5 empty] | Mtg Hole Details |  |  |  |  | Actuator Details
Damper ID | Damper Qty | Damper Diameter (inches) | Damper Design Pressure (in-wg) | Damper Material (Painted, 304SS, 316SS) | Basis of Design | Mtg Holes Required? (Y or N) | Qty of Holes | Hole Dia | Bolt Circle Dia | straddling Vertical CL or On Vertical CL | Actuator Type | Power Supply | Actuator Operation (PO/PC or Spring return) | If Spring return, fail open or fail closed | Auxiliary Switches Required (Y or N) | Nema Enclosure (1, 4, 4x, 7 or 9)
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
|  |  | 40 |  | Greenheck HBTR-551
Suggested Construction Notes: | [5 empty] | Mounting Hole Note: |  |  |  |  | Actuator Types:
Dampers shall be rated to 40 in-wg pressure | [5 empty] | "Manufacturer Standard" is a valid entry |  |  |  |  | Electric: 24VAC, 24VDC, 120VAC, 230VAC
Dampers shall be tested to AMCA 500D for bubble tight effectiveness before shipment | [10 empty] | Pneumatic: 80PSI
Manufacture Dampers in an ISO9001 certified facility | [10 empty] | Manual: Quadrant, Handwheel, Chainwheel
Design Temperature is a maximum temperature of 250°F | [10 empty] | Bracket Only: supplied with (2) mtg angles for field supplied actuators.
Dampers shall have fully welded construction and have full length damper shafts
Dampers shall have been prototype tested to 10,000 open and closed cycle tests to confirm durability | [10 empty] | Actuator Notes:
Dampers shall have double gland shaft seals. Press-fit lip seals are not acceptable. | [10 empty] | bracket-only option works well for commercial grade actuators, field supplied industrial actuators are not recommended.
Basis of Design: Greenheck, Model HBTR-551 | [10 empty] | Power Open/Power Closed actuator option will Fail In Place on loss of power